## Slide 1: A new fire compartment system in tunnel
INFN - LNGS
<number>
The case of The Gran Sasso National Laboratory
Andrea Basti – INFN – National Laboratory of Gran Sasso (Operation and Maintenance Service)
Dino Franciotti – INFN – National Laboratory of Gran Sasso (Operation and Maintenance Service)
Gabriele Bucciarelli – INFN – National Laboratory of Gran Sasso (Operation and Maintenance Service)
Graziano Panella – INFN – National Laboratory of Gran Sasso (Operation and Maintenance Service)
Notes: <number>

## Slide 2
INFN - LNGS
<number>
The aim of the study was:
Validation an eventually improvement of an existing cooling plant of fire proof door called Niagara (for the huge quantity of water used) by means of CFD software

## Slide 3: General Information on the Gran Sasso National Laboratory
INFN - LNGS
<number>
Geographic position
Under the mountain of Gran Sasso
Alongside one of the 2 fornices constituting the Gran Sasso highway tunnel
In the middle of 10 Km highway tunnel A24 Teramo - L’Aquila - Rome
Reason
1400 meters of rock are a perfect filter to screen huge number of particles that hit the land surface
Experimental
Mainly Neutrino’s physics research
Notes: <number>

## Slide 4: Necessary Requirements of fire resistant compartments
INFN - LNGS
<number>
Structural Resistance (R)
Smoke Seals (E)
Heat Insulation (I)
But for how much time long? and under which conditions?
Critical location of LNGS inside the A24 Highway tunnel
Notes: <number>

## Slide 5: General Information on the Gran Sasso National Laboratory
INFN - LNGS
<number>
Laboratory configuration
3 Big Hall (hall A, hall B, hall C) of 25.000 m3 each.
Service tunnels
3 Connection tunnels (2 carriageable and 1 pedestrians) with roadway tunnel
2 roadways tunnels (one Teramo direction and one L’Aquila direction)
Emergency plan solution (approved by authority)
Separation between LNGS and highway tunnel by means of fire resistant compartments
Notes: <number>

## Slide 6: Traditional requirements of the fire proof door
INFN - LNGS
<number>
Structural Resistance (R) under ISO 834 curve
Smoke Seals (E) under ISO 834 curve
Heat Insulation (I) under ISO 834 curve
Time 15 – 20 – 30 – 45 – 60 – 90 – 120 – 180 – 240 – 360 min.
ISO 834 curve
Critical location of LNGS inside the A24 Highway tunnel
Notes: <number>

## Slide 7
INFN - LNGS
<number>
UNI 11076 RWS curve
Necessary requirements of the fire proof door in tunnel
Structural Resistance (R), Smoke Seals (E), Heat Insulation (I)
should be under UNI 11076 curve because this curve represent the fire standard curve used in tunnels
Time 15 – 20 – 30 – 45 – 60 – 90 – 120 – 180 – 240 – 360 How many minutes ?
Critical location of LNGS inside the A24 Highway tunnel
Notes: <number>

## Slide 8: Critical location of LNGS inside the A24 Highway tunnel
INFN - LNGS
<number>
There are some difficulties to extimate the necessary time requirements that the fire proof door in tunnel should have to consent the Fire Brigades Assistance
REI requirements should be 120 minutes for Italy and some European Countries
REI requirements should be 180 minutes for Austria and Switzerland
How many minutes ?
180 minutes are approved by authorithy but is it ok?
Notes: <number>

## Slide 9: A solution maybe to increase as much as possible REI requirements
INFN - LNGS
<number>
What we call “Niagara” is a cooling plant on the existing fire proof doors that separate highway tunnel from LNGS
The increase of REI requirement is not easy to get, considering the high temperature and difficulty in removing hot smoke
Critical location of LNGS inside the A24 Highway tunnel
Notes: <number>

## Slide 10: “Niagara “- General Description of the plant
INFN - LNGS
<number>
Dimensions
Inner width 5.10 mt.
Inner high 4.60 mt.
Total diameter (pipe + heat insulator material and aluminium sheet) 0.30 mt.
On that pipeline 7 nozzles have been placed
Tree on the architrave
One at 1.6 mt from the floor on each pier (total: 2 nozzles)
One on the basement of each pier (total: 2 nozzles)
Notes: <number>

## Slide 11: “Niagara “- General Description of the plant
INFN - LNGS
<number>
Nozzles type were
Five Cone adjustable nozzles AISI 316 diameter ¾“ Flow rate 190 litres/min. at 4 bars
Two fan nozzles AISI 316 diameter ½“ Flow rate 35 litres/min. at 4 bars
Nozzles distribution
Cone adjustable nozzles are located tree on the architrave and two at 1.6m on the floor
Fan nozzles are located on the basement
Notes: <number>

## Slide 12: “Niagara “- General Description of the plant
INFN - LNGS
<number>
Cone adjustable nozzle
Fan nozzle
Niagara is located 3m far from the door to be protected
Notes: <number>

## Slide 13
INFN - LNGS
<number>
“Niagara “- General Description of the plant
Fan nozzles have the dual function:
cooling the foundation
clearing the water column that tends to accumulate in the piers up to 1.6 meters in height
Notes: <number>

## Slide 14
INFN - LNGS
<number>
“Niagara “- General Description of the plant
Water system adduction
“Niagara” system uses water dripping on rock (100 litres/sec).
Water adduction for the nozzles is via two pipes that pass through a reinforced concrete wall about 50 cm thick that supports fire proof door .
Water is pressurized to 8 bars, by a group of 4 pumps, 1500 litres per minute each, using a 8” pipe protected by a sandwich insulation.
The four pumps can be operated manually or through the detection of 9 temperature sensors placed on the external face of the door.
The 9 temperature sensors open the circuit when the temperature rises from about 14°C (constant temperature of the rock during the year) to 50°C, or by the sudden temperature increase of 2°C per minute.
Notes: <number>

## Slide 15
INFN - LNGS
<number>
“Niagara “- General Description of the plant
Water system adduction
The pumps that pressurize the system are electrically powered by a redundant system in low voltage backed up by a general Diesel Generator. In case of failure of main supply the pumps can be fed and by a local diesel generator.
On the water supply main circuit that serves “Niagara”, a pressure reducer calibrated at 4 bars has been installed.
The excess of water is collected by grids interposed between “Niagara” and highway.
Notes: <number>

## Slide 16
INFN - LNGS
<number>
Simulations with CFD software: Description of the Model
Overview on the CFD calculation
The software used for this CFD simulation is NIST’s Fire Dynamic Simulator (Mc Grattan et al. 2001a, b)
FDS was developed to specifically address fire-hazard scenarios
This software predicts smoke and/or air flow movement caused by fire, wind, ventilation systems and other sources of momentum.
To visualize the predictions generated by NIST FDS can be used Smokeview (Mc Grattan & Forney 2001c)
FDS solves a form of the Navier-Stokes equations appropriate for low-speed, thermally driven flows of smoke and hot gases generated in a fire.
Smokeview visualizes FDS computed data by animating time dependent particle flow, 2D slice contours and surface boundary contours. Data at a particular time may also be visualized using 2D or 3D contour plots or vector plots.
Notes: <number>

## Slide 17
INFN - LNGS
<number>
Simulations with CFD software: Description of the Model
D* : characteristic diameter of fire;
Q : heat release total rate, kW;
 : density at room temperature, kg/m3;
cp : specific heat of gas, kJ/kg°K;
T : room temperature, °K
In our simulation
T=283 °K
=1.2 kg/m3
cp =1.0 kJ/kg°K
Q = 200.000 kW
it results D* =8.12m.
Therefore, it is assumed an average size of the discretization at 10% D*80cm
Modelling of the geometry in FDS
Cell discretization
Notes: <number>

## Slide 18
INFN - LNGS
<number>
The volume is divided into two different types of mesh
on the highway tunnel the dimension of each cubic cell is 100 cm
on Niagara the dimension of each cubic cell is 20 cm
Total amount of cells are 85,600 cells
Simulations with CFD software: Description of the Model
Modelling of the geometry in FDS
Notes: <number>

## Slide 19
INFN - LNGS
<number>
Simulations with CFD software: Description of the Model
Modelling of the geometry in FDS
TUNNEL MATERIALS: Adiabatic Surface
VENTILATION INSIDE THE TUNNEL: 2m/s on the “VENT” input and to be an “OPEN VENT” in output
DIMENSION OF THE RADIATING SURFACE: 6m x 6m = 36 m2
HRR PEAK POWER CURVE HGV (Hard Good Vehicle): 220MW
HRRUA Heat Release Rate for Unit Area: 6111 Kw/m2
BURNT MATERIAL: Kerosene
POSITION OF THE PROBES: Along the tunnel that access the laboratory has been inserted a row of probes every 5 meters in plant and for each row a probe in every meter up to the keystone of the tunnel. Along the highway tunnel has been inserted two rows of probes before and after fire.
TYPES OF PROBES: Temperature of the gas, oxygen, carbon monoxide, carbon dioxide, nitrogen, hydrogen, pressure, water vapor and radiant energy.
HEAT DETECTOR: 9 Heat detector have been placed on the external face of the door according to real situation. The heat detector open the circuit when the temperature rises from 14°C to 50°C
Notes: <number>

## Slide 20
INFN - LNGS
<number>
Simulations with CFD software: Description of the Model
Modelling of the geometry in FDS
Notes: <number>

## Slide 21
INFN - LNGS
<number>
The HRR from the four large-scale Runehamar fire tests with HGV-trailer fire load
Simulations with CFD software: Description of the Model
Geometry’s modelling in FDS
Notes: <number>

## Slide 22
INFN - LNGS
<number>
Simulations with CFD software: Description of the Model
Results’ analysis
Duration of simulation:
3600 seconds
Maximum temperature reached on the door:
227°C at 1190 seconds
Notes: <number>

## Slide 23
INFN - LNGS
<number>
1) Temperature on the fire door exceeded 100°C
(Temperature of vaporization of water)
There is a fumes flow from the central part of the door towards the highway tunnel
There are areas of overpressure on the door
Nozzle pressure of 4 bars with flow rate of 233 l/min at speed of 13.5 m/s could not have enough strength to reach the surface of the door
2) Water cooling effect was lower in the central area while temperature of the central part of the door was not higher than of the rest of the door
Problems
Considerations
Simulations with CFD software: Description of the Model
Results’ analysis
Notes: <number>

## Slide 24
INFN - LNGS
<number>
Water cooling diagram for unit area on the fire proof door
Analysis of results
Accumulated Mass diagram for unit area on the fire proof door
Simulations with CFD software: Description of the Model
Notes: <number>

## Slide 25
INFN - LNGS
<number>
Suggested improvements
To solve the problem of the overpressure on the fire proof door on the top of “Niagara”, two additional nozzles with an opening angle less than the others and with a greater efflux speed.
The system is now able to provide a water film of few mm on the door so ensuring a REI requirements as long as water is available
Notes: <number>

## Slide 26
INFN - LNGS
<number>
Suggested improvements
1) In the following situation all Nozzles have been tilted 15° upward in order to optimize water delivered to the door
2) Added nozzles have been tilted 10° upward
3) On the fire proof door, the flow rates have been increased considering also the flow rate required to cool the other two doors and not exceeding the max flow rate available (100 litres/s)
Position of the added nozzles
Type BTF 3195 XX Steel AISI 316
Knowing flow and section of the nozzle we easily get the water outflow speed
4) The water pressure inside the pipe was increased from 4 bar to 6 bar
Notes: <number>

## Slide 27
INFN - LNGS
<number>
Suggested improvements
The simulation has been made again modelling and adding in FDS the two new nozzles
Duration of simulation:
2500 seconds
Maximum temperature reached on the door:
90°C at 1051 seconds
Notes: <number>

## Slide 28
INFN - LNGS
<number>
Duration of simulation:
3600 seconds
Maximum temperature reached on the door:
680°C at 1051 seconds
Fire proof door condition without “Niagara”
The simulation has been made again without “Niagara”
Notes: <number>

## Slide 29
INFN - LNGS
<number>
Comparison between the system with and without “Niagara”
With “Niagara” max temperature 90°C
Without “Niagara” max temperature 680°C
Notes: <number>

## Slide 30
INFN - LNGS
<number>
Comparison between the system with and without “Niagara”
With “Niagara”
max incident heat flux 7 Kw/mq
Without “Niagara”
max incident heat flux 40 Kw/mq
Notes: <number>

## Slide 31
INFN - LNGS
<number>
Conclusions
Results’ analysis
The results’ analysis have showed the potency of “Niagara” with the two nozzles added.
  on the fire proof door the temperature don’t excedeed 90 °C so that always exist during this kind of fire a water film that protect the door from high temperature.
  on the volume in proximity of the fire proof door the incident heat flux radiation don’t excedeed 7 Kw/mq
The change to “Niagara” system will be realized in the current year and actually the process patent registration is now pending

## Slide 32
INFN - LNGS
<number>
Thank you for your attention!
Andrea Basti – INFN – andrea.basti@lngs.infn.it
Dino Franciotti – INFN – dino.franciotti@lngs.infn.it
Gabriele Bucciarelli – INFN – gabriele.bucciarelli@lngs.infn.it
Graziano Panella – INFN – graziano.panella@lngs.infn.it
Notes: <number>